## Sheet1
Run | Reference |  | Type of Cell | Cathode Chemistry | Solvents | Initial SOC | Failure Test | Total Gas Volume (L) |  | Voltage | Amp-Hour | Energy Stored (Wh) | Mass Battery (g) | L/Wh | Pmax (psi) | Notes | Species Composition by % Volume or % mol | [11 empty] | Not in Cantera | [17 empty] | EMC | DMC | EC | DEC |  | Flamspedd
Execute | Ref-Author | Ref-Year | Format | Chemistry | Electrolyte | SOC | Failure | GasVol | WetGasVolume | Voltage | A-hr | W-hr | Mass | L/Wh | Pmax | Notes | CO2 | CO | H2 | CH4 | C2H4 | C2H6 | C3H8 | N2 | O2 | CH3OH | THC | H2O | Other | C2H2 | C3H6 | C4H10 | C4H102 | C4H8 | C5H12 | C5H123 | C6H6 | C7H8 | C8H10 | (CH3)2C6H4 | C2H5F | CH3OCH3 | CH3OCHO | C2H5OH | CH3F | PF3 | C4H8O3 | C3H6O3 | C3H4O3 | C5H10O3 | Column4 | Phi=1
| Abraham | 2006 | 18650 | NCA |  | 100 | Thermal-Abuse (ARC) | 0.0125 | [7 empty] | Punctured Cell | Emailed for Data
| Abraham | 2006 | 18650 | NCA | EC:EMC | 100 | Thermal-Abuse (ARC) | 0.0045 |  | 4.1 | 1 | 4.1 |  |  |  | Vented Cell
Done | Archibald | 12_29_2020 | Cylindrical - K2 24 cell array | LFP |  | 100 | Thermal Abuse | 33.5 |  | 12.8 | 22.2 | 284.16 |  | 0.11789 |  |  | 24 | 7.8 | 42 | 7.6 | 4.5 | 1.78 | 3.7 | 0 | 0 |  |  |  | 8.62
Syngas | Bouvet | 2011 | Syngas | 50-50_H2_CO | [12 empty] | 0 | 50 | 50 | 0
| Doughty | 2005 | 18650 | NCA | EC:EMC | 100 | Thermal-Abuse (ARC) |  |  | 4.1 | [5 empty] | 18650 with 2% VEC and 5% TPP | Emailed for data
| Doughty | 2005 | 18650 | NCA | EC:EMC | 100 | Thermal-Abuse (ARC) |  |  | 4.1 | [5 empty] | 18650 Baseline Test
| Doughty | 2005 | 18650 | NCA | EC:EMC | 100 | Thermal-Abuse (ARC) |  |  | 4.1 | [5 empty] | 18650 with 2% VEC
| Doughty | 2005 | 18650 | NCA | EC:EMC | 100 | Thermal-Abuse (ARC) |  |  | 4.1 | [5 empty] | Cell with 6% GDR Anode
| Doughty | 2005 | 18650 | NCA | EC:PC:EMC | 100 | Thermal-Abuse (ARC) |  |  | 4.1 | [5 empty] | Cell with 6% GDR Anode and EC/PC/EMC + 2% VEC electrolyte
Done | Essl | 2020 | Pouch | NMC-Pouch-60Ah-Thermal | EC:EMC | 100 | Thermal Abuse | 93.6 |  | 3.6 | 60 | 216 | 864 | 0.43333 |  |  | 30 | 26 | 15 | 5 | 10 | 0 | [5 empty] | 4 | 6 | 0 |  | 1 | [14 empty] | 3 | 0 | 0
Done | Essl | 2020 | Pouch | NMC/LMO-41Ah | EC:DEC:DMC(48:48:4) | 100 | Thermal Abuse | 57 |  | 3.8 | 41 | 155.8 | 865 | 0.36585 |  |  | 38.33 | 16.59 | 22.93 | 3.46 | 5.88 | 0.99 | 0 | 0 | [5 empty] | 0.05 |  | 1.26 | [14 empty] | 0 | 0 | 0 | 2.69
No | Essl | 2020 | Pouch | NMC/LMO-41Ah |  | 30 | Thermal Abuse | 13 |  | 3.8 | 41 | 155.8 | 865 | 0.08344 |  |  | 47.73 | 5.15 | 4.47 | 0.52 | 2.93 | 0.36 | 0 |  |  |  |  | 7.55 |  | 0.12 |  | 0 | [17 empty] | 20.72
No | Essl | 2020 | Pouch | NMC/LMO-41Ah |  | 0 | Thermal Abuse | 10 |  | 3.8 | 41 | 155.8 | 865 | 0.064185 | [8 empty] | 0.5 |  |  |  |  | 17.5
Done | Essl-NailPen | 2020 | Prismatic | NMC-Prismatic-60Ah-NailPen | EC:DMC:EMC | 100 | Nail Penetration | 106.2 |  | 3.6 | 60 | 216 | 960 | 0.49167 |  |  | 24 | 23 | 20 | 5 | 7 | 0 | [5 empty] | 3 | 15 | 0 |  | 1 | [14 empty] | 0 | 2 | 0
Done | Essl-NailPen | 2020 | Pouch | NMC-Pouch-60Ah-NailPen | EC:EMC | 100 | Nail Penetration | 102.6 |  | 3.6 | 60 | 216 | 864 | 0.475 |  |  | 30 | 22 | 23 | 3 | 14 | 0 | [5 empty] | 3 | 4 | 0 |  | 1 | [14 empty] | 0 | 0 | 0
Done | Essl-OCH | 2020 | Pouch | NMC-Pouch-60Ah-OCH | EC:EMC | 146 | Overcharge | 165.6 |  | 3.6 | 60 | 216 | 864 | 0.76667 |  |  | 20 | 33 | 26 | 5 | 8 | 1 | [5 empty] | 3 | 4 | 0 |  | 0 | [14 empty] | 0 | 0 | 0
Done | Essl-OCH | 2020 | Prismatic | NMC-Prismatic-60Ah-OCH | EC:DMC:EMC | 147 | Overcharge | 159 |  | 3.6 | 60 | 216 | 960 | 0.73611 |  |  | 20 | 30 | 27 | 7 | 4 | 1 | [5 empty] | 3 | 8 | 0 |  | 0 | [14 empty] | 0 | 0 | 0
Done | Essl-Thermal | 2020 | Prismatic | NMC-Prismatic-60Ah-Thermal | EC:DMC:EMC | 100 | Thermal Abuse | 93.6 |  | 3.6 | 60 | 216 | 960 | 0.43333 |  |  | 21 | 30 | 15 | 5 | 5 | 0 | [5 empty] | 4 | 14 | 0 |  | 2 | [14 empty] | 1 | 2 | 1
Done | FAA | 2016 | 18650 | LCO |  | 90 | Thermal-Abuse (Cone-calorimeter) | 5.23 | [7 empty] | Tests conducted at cabin pressure at altitude (10psia), compositions are from powerpoint presentation, assuming that the remaining gas is CO2 since only the volumes for hydrogen, CO and THC were given along with the total volumes | 37.8585 | 32.1224 | 19.3117 | [7 empty] | 10.7075
Done | FAA | 2016 | 18650 | LCO |  | 70 | Thermal-Abuse (Cone-calorimeter) | 4.24 | [7 empty] | Tests conducted at cabin pressure at altitude (10psia), compositions are from powerpoint presentation, assuming that the remaining gas is CO2 since only the volumes for hydrogen, CO and THC were given along with the total volumes | 40.8019 | 28.3019 | 20.0472 | [7 empty] | 10.8491
Done | FAA | 2016 | 18650 | LCO |  | 80 | Thermal-Abuse (Cone-calorimeter) | 5.05 | [7 empty] | Tests conducted at cabin pressure at altitude (10psia), compositions are from powerpoint presentation, assuming that the remaining gas is CO2 since only the volumes for hydrogen, CO and THC were given along with the total volumes | 41.5842 | 29.901 | 18.4158 | [7 empty] | 10.099
Done | FAA | 2016 | 18650 | LCO |  | 100 | Thermal-Abuse (Cone-calorimeter) | 7.85 | [6 empty] | 72.3 | Tests conducted at cabin pressure at altitude (10psia), compositions are from powerpoint presentation, assuming that the remaining gas is CO2 since only the volumes for hydrogen, CO and THC were given along with the total volumes | 44.4586 | 27.1338 | 19.4904 | [7 empty] | 8.9172
Done | FAA | 2016 | 18650 | LCO |  | 60 | Thermal-Abuse (Cone-calorimeter) | 2.81 | [7 empty] | Tests conducted at cabin pressure at altitude (10psia), compositions are from powerpoint presentation, assuming that the remaining gas is CO2 since only the volumes for hydrogen, CO and THC were given along with the total volumes | 55.1601 | 8.5409 | 23.4875 | [7 empty] | 12.8114
Done | FAA | 2016 | 18650 | LCO |  | 50 | Thermal-Abuse (Cone-calorimeter) | 2.25 | [6 empty] | 70.1 | Tests conducted at cabin pressure at altitude (10psia), compositions are from powerpoint presentation, assuming that the remaining gas is CO2 since only the volumes for hydrogen, CO and THC were given along with the total volumes | 57.7778 | 5.3333 | 19.1111 | [7 empty] | 17.7778
Done | FAA | 2016 | 18650 | LCO |  | 40 | Thermal-Abuse (Cone-calorimeter) | 2.09 | [7 empty] | Tests conducted at cabin pressure at altitude (10psia), compositions are from powerpoint presentation, assuming that the remaining gas is CO2 since only the volumes for hydrogen, CO and THC were given along with the total volumes | 57.8947 | 4.7847 | 21.0526 | [7 empty] | 16.2679
Done | FAA | 2016 | 18650 | LCO |  | 30 | Thermal-Abuse (Cone-calorimeter) | 1.5 | [7 empty] | Tests conducted at cabin pressure at altitude (10psia), compositions are from powerpoint presentation, assuming that the remaining gas is CO2 since only the volumes for hydrogen, CO and THC were given along with the total volumes | 75.6667 | 2.3333 | 6.6667 | [7 empty] | 15.3333
Done | FAA | 2016 | 18650 | LCO |  | 20 | Thermal-Abuse (Cone-calorimeter) | 1.32 | [7 empty] | Tests conducted at cabin pressure at altitude (10psia), compositions are from powerpoint presentation, assuming that the remaining gas is CO2 since only the volumes for hydrogen, CO and THC were given along with the total volumes | 79.5455 | 2.2727 | 4.5455 | [7 empty] | 13.6364
Done | FAA | 2016 | 18650 | LCO |  | 10 | Thermal-Abuse (Cone-calorimeter) | 1.04 | [7 empty] | Tests conducted at cabin pressure at altitude (10psia), compositions are from powerpoint presentation, assuming that the remaining gas is CO2 since only the volumes for hydrogen, CO and THC were given along with the total volumes | 82.6923 | 1.9231 | 3.8462 | [7 empty] | 11.5385
Done | Fernandes | 2018 | Cylindrical 26650 | LFP | DMC:EMC:EC:PC | 190 | Overcharged (Explosion Proof Room) |  |  |  | 2.5 |  | 75.41 |  |  | 190% SOC before rupturing, 300 mL sample tested, average used | 46.77 | 4.91 | 23.7 | 1.51 | 10.04 | 0.63 |  |  |  | 0.28 |  |  | 0.31 |  | 0.31 | [9 empty] | 4.56 | 3.09 | 1.94 | 1.06 | 0.9 | 0.42
| Fri | 2016 | Pouch | NMC |  | OCH | Thermal Abuse on Overcharged Cells (Combustion Chamber) |  |  |  | 10
| Fu | 2015 | 18650 | LCO |  | 70 | Thermal-Abuse (Cone-calorimeter) |  |  |  | 2.6
| Fu | 2016 | 18650 | LCO |  | 65 | Thermal-Abuse (Cone-calorimeter) |  |  |  | 2.6
| Fu | 2015 | 18650 | LCO |  | 50 | Thermal-Abuse (Cone-calorimeter) |  |  |  | 2.6
| Fu | 2015 | 18650 | LCO |  | 0 | Thermal-Abuse (Cone-calorimeter) |  |  |  | 2.6
| Fu | 2015 | 18650 | LCO |  | 100 | Thermal-Abuse (Cone-calorimeter) |  |  |  | 2.6 |  |  |  |  | Goes into detail about time to ignition for different SOC/Heat Flux
Done | Golubkov | 2014 | 18650 | LCO/NMC | DMC:EMC:EC | 100 | Thermal Abuse (Reactor Chamber) | 6.5659 |  | 3.8 | 2.6 | 9.88 | 44.3 | 0.66457 |  | * Not sure if charging regimen, leaves them at exactly 100% | 24.9 | 27.6 | 30 | 8.6 | 7.7 | 1.2
| Golubkov | 2015 | 18650 | LFP | DMC:EMC:EC:PC:MPC | 0 | Thermal Abuse |  |  | 3.5 | 1.1 | 3.85 |  |  |  |  | 93.5 | 1.8 | 2.7 | 0.7 | 0.7 | 0.7
Done | Golubkov | 2015 | 18650 | LFP | DMC:EMC:EC:PC:MPC | 25 | Thermal Abuse | [9 empty] | 85.3 | 3.1 | 7.1 | 1.2 | 3.1 | 0.2
Done | Golubkov | 2015 | 18650 | LFP | DMC:EMC:EC:PC:MPC | 50 | Thermal Abuse | [9 empty] | 66.2 | 4.8 | 20.8 | 1.6 | 6.6
Done | Golubkov | 2015 | 18650 | LFP | DMC:EMC:EC:PC:MPC | 75 | Thermal Abuse | [9 empty] | 62.6 | 6.4 | 21.8 | 1.9 | 6.3 | 1
Done | Golubkov | 2014 | 18650 | LFP | DMC:EC:PC | 100 | Thermal Abuse (Reactor Chamber) | 1.2389 |  | 3.3 | 1.1 | 3.63 | 38.8 | 0.34128 |  | * Not sure if charging regimen, leaves them at exactly 100% | 53 | 4.8 | 30.9 | 4.1 | 6.8 | 0.3
Done | Golubkov | 2014 | 18650 | NMC | DMC:EMC:EC | 100 | Thermal Abuse (Reactor Chamber) | 3.6918 |  | 3.8 | 1.5 | 5.7 | 43 | 0.64768 |  | * Not sure if charging regimen, leaves them at exactly 100% | 41.2 | 13 | 30.8 | 6.8 | 8.2
| Golubkov | 2015 | 18650 | LFP | DMC:EMC:EC:PC:MPC | 115 | Thermal Abuse | [9 empty] | 52.2 | 6.4 | 34 | 2.6 | 4.7 | 0.1
Done | Golubkov | 2015 | 18650 | LFP | DMC:EMC:EC:PC:MPC | 130 | Thermal Abuse | [9 empty] | 55.8 | 7.7 | 30.1 | 6.4
| Golubkov | 2015 | 18650 | NCA | DMC:EMC:EC:PC:MPC | 0 | Thermal Abuse |  |  | 4.2 | 3.5 | 14.7 |  |  |  |  | 94.6 | 1.6 | 1.7 | 1.6 | 0.3
| Golubkov | 2015 | 18650 | NCA | DMC:EMC:EC:PC:MPC | 0 | Thermal Abuse | [9 empty] | 94.7 | 1.9 | 1.8 | 1.2 | 0.4
| Golubkov | 2015 | 18650 | NCA | DMC:EMC:EC:PC:MPC | 0 | Thermal Abuse | [9 empty] | 96 | 1.5 | 1.2 | 1.1 | 0.2
| Golubkov | 2015 | 18650 | NCA | DMC:EMC:EC:PC:MPC | 0 | Thermal Abuse | [9 empty] | 96.2 | 1.1 | 0.9 | 1.4 | 0.3
| Golubkov | 2015 | 18650 | NCA | DMC:EMC:EC:PC:MPC | 0 | Thermal Abuse | [9 empty] | 96.6 | 1 | 0.8 | 1.3 | 0.3
| Golubkov | 2015 | 18650 | NCA | DMC:EMC:EC:PC:MPC | 25 | Thermal Abuse | [9 empty] | 62.7 | 5.5 | 15.5 | 8.7 | 7.5
Done | Golubkov | 2015 | 18650 | NCA | DMC:EMC:EC:PC:MPC | 50 | Thermal Abuse | [9 empty] | 33.8 | 39.9 | 17.5 | 5.2 | 3.2 | 0.4
Done | Golubkov | 2015 | 18650 | NCA | DMC:EMC:EC:PC:MPC | 75 | Thermal Abuse | [9 empty] | 20.8 | 43.7 | 24.2 | 7.5 | 3.3 | 0.5
Done | Golubkov | 2015 | 18650 | LFP | DMC:EMC:EC:PC:MPC | 100 | Thermal Abuse | 0.79286 |  | 3.2 | 1.1 | 3.52 |  | 0.22525 |  |  | 48.3 | 9.1 | 29.4 | 5.4 | 7.2 | 0.5
| Golubkov | 2015 | 18650 | NCA | DMC:EMC:EC:PC:MPC | 112 | Thermal Abuse | [9 empty] | 18.8 | 48.1 | 25.1 | 5.9 | 2.1
Done | Golubkov | 2015 | 18650 | NCA | DMC:EMC:EC:PC:MPC | 120 | Thermal Abuse | [9 empty] | 20.8 | 48.7 | 23.5 | 5.4 | 1.6
Done | Golubkov | 2015 | 18650 | NCA | DMC:EMC:EC:PC:MPC | 127 | Thermal Abuse | [9 empty] | 16.2 | 46.6 | 28.8 | 6.4 | 1.3 | 0.3
| Golubkov | 2015 | 18650 | NCA | DMC:EMC:EC:PC:MPC | 132 | Thermal Abuse | [9 empty] | 18.9 | 49.2 | 25.8 | 4.7 | 1.4
| Golubkov | 2015 | 18650 | NCA | DMC:EMC:EC:PC:MPC | 143 | Thermal Abuse | [9 empty] | 22 | 43.4 | 26.2 | 6.9 | 1.5
Done | Golubkov | 2015 | 18650 | NCA | DMC:EMC:EC:PC:MPC | 100 | Thermal Abuse | 7.78 |  | 3.6 | 3.35 | 12.06 |  | 0.64511 |  |  | 17.5 | 44 | 26.1 | 8.9 | 2.7 | 0.9
Done | Golubkov | 2015 | 18650 | NCA1 | DMC:EMC:EC:PC:MPC | 100 | Thermal Abuse | 6.0456 |  | 3.6 | 3.35 | 12.06 |  | 0.50129 |  |  | 22.7 | 41.5 | 28.5 | 5.9 | 1.3 | 0.3
Done | Golubkov | 2015 | 18650 | NCA2 | DMC:EMC:EC:PC:MPC | 100 | Thermal Abuse | 6.7622 |  | 3.6 | 3.35 | 12.06 |  | 0.56071 |  |  | 19.7 | 48.9 | 22.6 | 6.6 | 2.4
Test | Hydrogen | 2021 |  | H2 | [14 empty] | 100
Done | Kennedy | 11_11_2019 | Prismatic_SDI | NMC |  | 100 |  | 221.6 | 231.5 | 3.68 | 95.6 | 351.808 | 2010 | 0.62989 |  |  | 29.9 | 21.3 | 30.6 | 7.2 | 5.6 | 1.76 | 2 | [5 empty] | 1.64
Done | Kennedy | 11_5_2019 | PouchArray_5x18 | LCO |  | 100 |  | 118.2 | 133.4 | 3.7 | 92.5 | 342.25 |  | 0.34536 |  |  | 31.9 | 23.9 | 26.8 | 4.8 | 7.1 | 1.26 | 2.4 | [5 empty] | 1.84
Done | Kennedy | 11_7_2019 | PouchArray_5x10 | LCO |  | 50 |  | 19.5 | 28.2 | 3.7 | 50 | 185 |  | 0.10541 |  |  | 33.2 | 6.8 | 36.1 | 5.1 | 3.8 | 1.28 | 4.6 | [5 empty] | 9.12
Done | Kennedy | 10_3_2019 | PouchArray_5x10 | LCO |  | 75 |  | 38 | 43.4 | 3.7 | 50 | 185 |  | 0.20541 |  |  | 41.3 | 6.3 | 32.5 | 5.8 | 3.3 | 1.11 | 5 | [5 empty] | 4.69
Done | Kennedy | 9_13_2019 | PouchArray_5x10 | LCO |  | 100 |  | 75 | 81.8 | 3.7 | 50 | 185 |  | 0.40541 |  |  | 43.5 | 13.9 | 24.5 | 4.8 | 2.7 | 0.77 | 0 | [5 empty] | 9.83
| Kong | 2005 | 18650 | LCO | EC:DEC | OCH | Overcharged |  |  | 4.2 | 1.1 | 4.62 |  |  |  | No off-gas compositions
| Kong | 2005 | 18650 | LFP |  | OCH | Overcharged |  |  | 3.65 | 1 | 4.62
| Kong | 2005 | 18650 | LMO |  | OCH | Overcharged |  |  | 4.3 | 0.7 | 3.01
| Kumia | 1999 | 18650 | LCO | PC:EMC:DEC:DMC | Varied | Cycled/Overcharged/Overdischarged at 25 C | 0.04021 |  | 4.2 | 1 | 4.2 |  | 0.0095738 |  | Varying Tests with different volumes of gases detected, the largest volume recorded | 71.2 | 0.6 |  | 21 |  | 3.2 | 0.8 | [7 empty] | 1
| Lammer | 2015 | 18650-MJ1 | NCA |  | 100 | Thermal Abuse |  |  | 3.5 |  |  | 46.35 |  |  | Deflagration | 9.76 | 37.22 | 43.15 | 6.97 | 2.69 | 0.06 | [7 empty] | 0.16
| Lammer | 2017 | 18650-35E | NCA |  | 100 | Thermal Abuse |  |  | 3.5 |  |  | 47.68 |  |  | Deflagration | 14.5 | 44 | 35.68 | 3.66 | 1.95 | 0.06 | [7 empty] | 0.14
| Lammer | 2017 | 18650-32A | NCA |  | 100 | Thermal Abuse |  |  | 3.2 |  |  | 48.62 |  |  | Deflagration | 20.4 | 58.41 | 15.94 | 2.5 | 2.44 | 0.09 | [7 empty] | 0.22
| Lammer | 2017 | 18650-32A | NCA |  | 100 | Thermal Abuse |  |  | 3.2 |  |  | 48.62 |  |  | 1st Venting | 82.19 | 0 | 2.43 | 0 | 9.32 | 6.06 | [7 empty] | 0
| Lammer | 2017 | 18650-35E | NCA |  | 100 | Thermal Abuse |  |  | 3.5 |  |  | 47.68 |  |  | Thermal Runaway | 87.24 | 0 | 3.87 | 0 | 4.2 | 4.7 | [7 empty] | 0
| Lammer | 2017 | 18650-32A | NCA |  | 100 | Thermal Abuse |  |  | 3.2 |  |  | 48.62 |  |  | Thermal Runaway | 95.56 | 0 | 3.71 | 0 | 0.74 | 0 | [7 empty] | 0
| Lammer | 2017 | 18650-MJ1 | NCA |  | 100 | Thermal Abuse |  |  | 3.5 |  |  | 46.35 |  |  | Thermal Runaway | 98.06 | 0 | 0.87 | 0 | 1.07 | 0 | [7 empty] | 0
| Lammer | 2017 | 18650-35E | NCA |  | 100 | Thermal Abuse |  |  | 3.5 |  |  | 47.68 |  |  | 1st Venting | 100 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0
| Lammer | 2017 | 18650-MJ1 | NCA |  | 100 | Thermal Abuse |  |  | 3.5 |  |  | 46.35 |  |  | 1st Venting | 100 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0
| Lapalame | 2014 | Syngas | S50M5 | [12 empty] | 0 | 47.5 | 47.5 | 5
| Lapalame | 2014 | Syngas | S50M20 | [12 empty] | 0 | 40 | 40 | 20
| Lapalame | 2014 | Syngas | S50M40 | [12 empty] | 0 | 30 | 30 | 40
| Lapalame | 2014 | Syngas | S50C10 | [12 empty] | 10 | 45 | 45 | 0
| Lapalame | 2014 | Syngas | S50C20 | [12 empty] | 20 | 40 | 40 | 0
| Lapalame | 2014 | Syngas | S50C30 | [12 empty] | 30 | 35 | 35 | 0
| Lapalame | 2014 | Syngas | S50C40 | [12 empty] | 40 | 30 | 30 | 0
| Larsson | 2017 | Cylindrical | Laptop Battery |  | 100 | Thermal Abuse (Fire Test Chamber) |  |  | 11.1 | 5.6 | 62.16 |  |  |  | Each laptop battery pack has 6 cells of type 18650; arranged 2 in parallel and 3 in series. 2 batteries per test
| Larsson | 2014 | 5x EiG ePLB-F007A | LFP |  | 100 | Thermal Abuse (Fire Test Chamber) |  |  |  | 35 |  | 1227.9 |  |  | Measured HF and POF3 off-gas, goes over HF release
| Larsson | 2014 | 5x EiG ePLB-F007A | LFP |  | 100 | Thermal Abuse (Fire Test Chamber) |  |  |  | 35 |  | 1229.7 |  |  | Measured HF and POF3 off-gas
| Larsson | 2014 | 5x EiG ePLB-F007A | LFP |  | 100 | Thermal Abuse (Fire Test Chamber) |  |  |  | 35 |  | 1229.3 |  |  | Measured HF and POF3 off-gas, included water mist
| Larsson | 2014 | 9x K2 LFP26650EV | LFP |  | 100 | Thermal Abuse (Fire Test Chamber) |  |  |  | 28.8 |  | 734.8 |  |  | Measured HF and POF3 off-gas
| Larsson | 2014 | 12x Lenovo laptop battery packs |  |  | 100 | Thermal Abuse (Fire Test Chamber) |  |  |  | 33.6 |  | 639 |  |  | Measured HF and POF3 off-gas
| Larsson | 2017 | Prismatic hard Al-can | LCO |  | 100 | Thermal Abuse (Fire Test Chamber) |  |  | 3.75 | 6.8 | 25.5 |  |  |  | 5-10 batteries per test, goes over HF Release
| Larsson | 2017 | Pouch | LFP |  | 100 | Thermal Abuse (Fire Test Chamber) |  |  | 3.2 | 20 | 64 |  |  |  | 2 batteries per test
| Larsson | 2017 | Pouch | LFP |  | 100 | Thermal Abuse (Fire Test Chamber) |  |  | 3.2 | 7 | 22.4 |  |  |  | 5 batteries per test
| Larsson | 2017 | Cylindrical | LFP |  | 100 | Thermal Abuse (Fire Test Chamber) |  |  | 3.2 | 3.2 | 10.24 |  |  |  | 9 batteries per test
| Larsson | 2017 | Cylindrical | LFP |  | 100 | Thermal Abuse (Fire Test Chamber) |  |  | 3.3 | 8 | 26.4 |  |  |  | 5 batteries per test
| Larsson | 2014 | 5x EiG ePLB-F007A | LFP |  | 50 | Thermal Abuse (Fire Test Chamber) |  |  |  | 35 |  | 1227.6 |  |  | Measured HF and POF3 off-gas
| Larsson | 2014 | 5x EiG ePLB-F007A | LFP |  | 0 | Thermal Abuse (Fire Test Chamber) |  |  |  | 35 |  | 1228.6 |  |  | Measured HF and POF3 off-gas
| Larsson | 2017 | Pouch | NCA-LATP |  | 100 | Thermal Abuse (Fire Test Chamber) |  |  | 2.3 | 30 | 69 |  |  |  | 2 batteries per test
Done | Liu | 2021 | Tianjin LiShen | LFP |  | 100 | [10 empty] | 35.5 | 22.3 | 29.6 | 6.9 | 5.7 | [7 empty] | -1.4211e-14
Test | Methane | 2019 | [17 empty] | 100
| Mon | 2016 | 18650 | LFP |  | OCH | Thermal Abuse on Overcharged Cells (Combustion Chamber)
| Ohsaki | 2005 | Prismatic 633048 | LCO | EC:EMC | OCH | Overcharged at 1 C Rate | 0.02301 |  | 3.7 | 0.65 | 2.405 | 25.5 | 0.0095676 |  | Unsure of battery voltage, looked up model number | 49.1091 | 5.2151 | 12.0382 | 14.7762 | 4.0852 | 14.7762
Test | Propane | 2019 | [20 empty] | 100
| Ribiere | 2011 | Pouch Cells | LMO | EC:DEC:DMC | 100, 50, 0 | Thermal-Abuse (Tewarson calorimeter) |  |  | 3.8 | 2.9 | 11 |  |  |  | Gives the mass of CO2, CO and the THC in ppm
| Roth | 2008 | 18650 | NCA | EC:EMC | 100 | Thermal-Abuse (ARC) | [8 empty] | 400 C | Emailed for Data
| Roth | 2008 | 18650 | NCA | EC:EMC | 100 | Thermal-Abuse (ARC) |  |  |  | 0.88 |  |  |  |  | 200 C
| Roth | 2008 | 18650 | NCA | EC:EMC | 100 | Thermal-Abuse (ARC) | [8 empty] | 300 C
| Somandepalli | 2014 | Pouch Cells | LCO | ED:DEC | 150 | Thermal Abuse (Combustion chamber) | 6 |  | 3.7 | 2.1 | 7.7 |  | 0.77 | 7.7 |  | 20.9 | 24.5 | 29.7 | 8.21 | 10.77 | 1.32 | 2.54 | [7 empty] | 0.01 | 0.133 | 0.39 | 0.6 | 0.04 | 0.3 | 0.33 | 0.05 | 0 | 0
Done | Somandepalli | 2014 | Pouch Cells | LCO | ED:DEC | 100 | Thermal Abuse (Combustion chamber) | 2.5 | [5 empty] | 0.32 | 7.1 |  | 30 | 22.9 | 27.7 | 6.39 | 2.19 | 1.16 | 0.26 | [7 empty] | 4.52 | 0.2 | 0.56 | 1.58 | 0.07 | 0.73 | 0.11 | 0.02 | 0 | 0
Done | Somandepalli | 2014 | Pouch Cells | LCO | ED:DEC | 50 | Thermal Abuse (Combustion chamber) | 0.8 | [5 empty] | 0.1 |  |  | 32 | 3.61 | 30 | 5.78 | 5.57 | 2.75 | 0.68 | [7 empty] | 8.16 | 0.41 | 0.67 | 2.55 | 0.45 | 1.94 | 0.14 | 0.06 | 0.01 | 0.01
| Spinner | 2015 | 18650 | LCO | DMC:EC:PC |  | Thermal Abuse on Overcharged Cells(Fire Test Chamber) | [8 empty] | Single and Hexagonal cell configuration, hot glued and hose-claps, gives ranges for CO2, CO, SO2, O2 and CH4 released in ppm
| Sun | 2016 | 18650 | LCO |  | OCH | Thermal Abuse on Overcharged Cells (Combustion Chamber) | [8 empty] | Gives some concentrations in ppm
| Sun | 2016 | 18650 | NMC |  | OCH | Thermal Abuse on Overcharged Cells (Combustion Chamber)
| Sun | 2016 | 18650 | LMO |  | OCH | Thermal Abuse on Overcharged Cells (Combustion Chamber)
| Sun | 2016 | Pouch | LMO |  | OCH | Thermal Abuse on Overcharged Cells (Combustion Chamber) |  |  |  | 10
Done | Viswanathan | 2020 | Pouch | LFP |  | 100 |  | 29 |  | 3.2 | 50 | 160 | 1180 | 0.18125 |  |  | 25.9 | 8.4 | 54.1 | [7 empty] | 11.5
Done | Viswanathan | 2020 | Pouch | NMC |  | 100 |  | 100 |  | 3.7 | 72.5 | 268.25 | 1200 | 0.37279 |  |  | 28.9 | 24.4 | 31.2 | [7 empty] | 15.5
| Yuan | 2015 | Prismatic | LFP | EC:DEC:EM | 190 | Overcharged |  |  | 5.1 | 32 | 163.2 |  |  |  |  | 58.4 | 31.7 |  | 0.53 | 3.97 | 0.81 | [6 empty] | 4.59
| Yuan | 2015 | Prismatic | LFP | EC:DEC:EM | 170 | Overcharged |  |  | 5.1 | 32 | 163.2 |  |  |  |  | 32.2 | 45.1 |  | 0.53 | 4.2 | 0.51 | [6 empty] | 17.99
| Yuan | 2015 | Prismatic | LFP | EC:DEC:EM | 180 | Overcharged |  |  | 5.1 | 32 | 163.2 |  |  |  |  | 39.9 | 43.3 |  | 0.4 | 7.9 | 0.8 | [6 empty] | 7.8
| Zheng | 2016 | Pouch | LFP | EC:DMC:EMC | 0 | Overdischarged (Glove Box) | [8 empty] | Gas species based on over-discharged battery (0.0 V) |  |  | 35.68 | 53.06 | 0.29 | 6.12 | 0.69 | 2.75 | 0.77 |  |  |  |  | 0.18
Syngas | Zhou | 2019 | Syngas | Basis | [12 empty] | 0 | 40 | 40 | 20
Syngas | Zhou | 2019 | Syngas | H2-60 | [12 empty] | 0 | 26.7 | 60 | 13.3
Syngas | Zhou | 2019 | Syngas | H2-80 | [12 empty] | 0 | 13.3 | 80 | 6.7
Syngas | Zhou | 2019 | Syngas | CO-60 | [12 empty] | 0 | 60 | 26.7 | 13.3
Syngas | Zhou | 2019 | Syngas | CO-80 | [12 empty] | 0 | 80 | 13.3 | 6.7
Syngas | Zhou | 2019 | Syngas | CH4-60 | [12 empty] | 0 | 20 | 20 | 60
Syngas | Zhou | 2019 | Syngas | CH4-80 | [12 empty] | 0 | 10 | 10 | 80